Amend Section 616 - Sprinkler System to read as follows:

“SECTION 616 - SPRINKLER SYSTEM

616.01	Description.     This work includes installing a sprinkler systems such as piping,  sprinkler heads,  valves,  automatic controllers,  remote  control valves,  booster pumps,  valve assembly units,  power and control wiring,  pullboxes,  and related equipment and materials at locations shown in the contract or as specified by the Engineer.

616.02	Materials.     Materials shall conform to the following:

Trench Backfill Material	703.21

Polyvinyl Chloride (PVC) Pipe	706.13

Dark Green Enamel Paint	708.03

Pullboxes	712.06(B)

Frames and Covers	712.07(A)

Sprinkler Heads	712.12

Valves	712.13

Pressure Regulators	712.14

Backflow Preventers	712.15

Precast Concrete Meter and Valve Boxes and Covers	712.23

Cables, Conductors and Wires for Irrigation System	712.34(C)

Automatic Controller	712.42(A)

Pump, Motor and Motor Controller	712.43

Springs for Sprinkler Risers	712.47

Electrical Appurtenances	712.48

Valve Boxes and Covers (Plastic and Concrete)	712.49

Switching Tensiometer	712.50

Rain Sensor Switch	712.52

Cullet Materials for Drainage System	717.04

Materials and equipment incorporated in the irrigation system shall be new and shall be of recognized standard quality.     The Engineer will inspect and test the materials according to the contract.

Electrical equipment shall conform to the NEMA Standards.     Electrical work shall conform to the National Electrical Code (the Code),  General Order No. 6 of the Hawaii Public Utilities Agreement,  local power company rules,  and local ordinances that may apply.

Sprinkler water lines under the roadway shall be PVC pipe,  Schedule 80 with threaded connections.

Concrete for reaction blocks,  pump foundations and jackets shall be Class B conforming to Section 601 - Structural Concrete.

Within 10 days following the award of contract,  submit a list of the irrigation equipment that the Contractor will use on the project.     The list shall be by name of manufacturer and catalog number.     The list of irrigation equipment shall include sprinkler heads,  valves,  irrigation control equipment,  booster pump units,  and pump controls as required for the irrigation system.

Materials will be subject to inspection by the Engineer.     Failure of the Engineer to note faulty material or workmanship during construction will not relieve responsibility by the Contractor for removing or replacing such materials and redoing the work at no cost to the State.

616.03	Construction Requirements.

(A)	Installation.

(1)	General.     The irrigation system shown in the contract is diagrammatic only.     Provide the pipe fittings or substitute other pipe fittings necessary to complete the connections shown in the contract.  Alterations and changes in the layout may occur to conform to the ground conditions and to obtain full and adequate coverage of water.  Do not change or alter the system as planned without prior acceptance by the Engineer.

Ream the pipes after being cut and clean and free the pipes from dirt or other foreign matter.     Make the  metal to metal screwed joints with an accepted non-soluble and nontoxic lubricant on the male thread only.

Excavate the necessary trenches and other openings a minimum of 18 inches of depth or to the required depth shown in the contract.     Excavate the additional depth and width where required,  to ease valves,  reaction blocks,  concrete jackets,  rock removal,  connections to other mains or to clear subsurface obstructions. Trenches shall be of sufficient width to permit snaking of plastic pipe not connected by rubber ring-type  fittings.     The Contractor need not snake the pipe connected with rubber ring-type fittings.

Trenches for plastic pipe shall be smooth and free of jagged rubble or sharp objects that will cause abrupt bending stresses and uneven weight distribution during backfilling operations.     Before backfilling the pipe line trenches in an area that the Contractor will water,:

(a)	pressure test that unit of the irrigation system and

(b)	modify the sprinkler locations if necessary to get complete and uniform coverage or flow.

Supply line trenches located next to curbs,  dikes,  and paved shoulders shall be at least four feet from said curbs,  dikes,  and paved shoulders.

Install reaction blocks according to the manufacturer's instructions and as specified by the Engineer.     Furnish a copy of the manufacturer's instructions to the Engineer before installing the pipes.

When installing supply lines through existing paved areas,  replace the subbase,  base,  and paving removed with material of equal quality.

Set the risers for sprinklers on slopes approximately perpendicular to the plane of the slope or half-way between perpendicular to slope and vertical for best coverage.     Install each series of sprinklers and adjust and test operate the nozzles to establish the location on the slope and proper angle of the risers.

If the location of a supply line interferes with the drilling of plant holes,  locate the plant holes to clear the supply lines.     Do not install supply lines through plant holes except in the installation of emitters or bubble heads.

Install the vertical spring action check valves on the sprinkler risers or swing joints shown in the contract or specified by the Engineer.

Before the Contractor removes or disturbs markers showing the location of existing cross-over conduits,  mark the conduit location on the pavement.

Connect the underground metallic pipes,  valves or fittings made of dissimilar metals through a dielectric coupling or bushing. Separate these pipes physically from other metal objects a minimum of one-eight inch.     The Contractor may require non-conducting spacers that will insure physical separation of pipe from foreign objects as decided by the Engineer.

Before any portion of the pipeline on the supply side of a control valve is backfilled,  expel the air from the line.  Then turn the water and maintain at full pressure for not less than 8 consecutive hours.     Also,  before any portion of the pipeline on the discharge side of a control valve is backfilled,  do a similar test except the test shall be for a duration of one hour.     Repair leaks that develop in the portion of the system installed by the Contractor and replace defective materials at no cost to the State.     Plug or cap the pipe where the Contractor will install sprinklers while making this test.     Then check the entire system for uniform and complete coverage after installing sprinklers.

After installing the pipe and testing the pipe properly according to the contract,  backfill and compact the trench in 6 inch layers according to Section 206 - Excavation and Backfill for Conduits and Structures.     Dispose of the remaining material.

In planting areas,  the Contractor may compact the backfill material by ponding or jetting with water until the backfill material,  after settlement,  is level with the surrounding soil.     Fill the pipeline with water before compacting the backfill material.

Backfill the pipe trenches so that sharp objects will not damage the pipe.     Do not place rocks directly on the pipe.

When backfilled area has settled,  refill and compact said area including furnishing,  applying,  and compacting the fill material.

When meeting solid rock,  excavate the rock:

(a)	to a depth 6 inches below the invert grade and

(b)	to a width four inches on each side of the pipe.

Backfill the space up to the invert with trench backfill material. Compact the trench backfill material firmly.

Install the pressure regulators and backflow  preventers according to the Plumbing Code of the respective County.

(2)	PVC Pipe.     Join the plastic pipe and fittings  by solvent cementing,  slip seat joints,  or threaded joints.     Cuts shall be square-end and clean.     When clamping the pipe,  protect the pipe from nicks and scouring by wrapping in canvas,  emery paper or other accepted  materials.

Install the plastic pipes and fittings according to the manufacturer's instructions and procedures.     Furnish a copy of the  printed instructions to the Engineer before installing the pipe.     The Contractor shall be responsible  for making arrangements with the pipe manufacturer for field assistance.

In making solvent cement joints,  do not apply pressure until the joints cure for an adequate time.

Screw the threaded joints and apply an accepted non-hardening,  putty-type joint compound.     Avoid undue strain on plastic material.     On plastic to steel connections,  make the steel connections first.     Tighten the threaded joints about one turn past hand-tight with a strap wrench.

Install the plastic pipes to allow for expansion and contraction as recommended by the manufacturer's instructions and procedures.

(3)	Valves and Valve Boxes.     Construct the valve manifolds shown in the contract.

If the contract shows multiple installations of valves in a large single valve box,  the Contractor may,  at its option,  install the valve in individual valve boxes.     Install the valves with a two inch clearance from valve box walls.

Install the valve boxes with their tops one inch above the surface of surrounding grade.     In concrete walks or traffic islands,  flush the top of the valve boxes with the surrounding grade.

The Contractor may substitute plastic valve boxes for portland cement concrete valve boxes.

(4)	Valve Keys.     Furnish to the Engineer upon completion of the project:

(a)	two long shank keys or wrenches for flow adjustment  of manual control valves and

(b)	two valve keys for four inch or larger gate valves.

(5)	Electric Automatic Controllers.     House each controller in a pedestal type enclosure.     Install the controller on a  portland  cement concrete foundation or wall mounted shown in the contract. The concrete for the foundation shall be Class B and shall conform to Section 601 - Structural Concrete.     The Engineer will permit hand mixing of foundation concrete.

Each controller shall have an individual neutral conductor to its respective valves.

Submit a complete maintenance and operations manual for each type of controller to the Engineer before the plant establishment period.

A complete schematic wiring diagram for each controller shall be a part of the maintenance manual.     The diagram shall show in detail the circuits and parts.     Also,  submit one copy of said diagram in a heavy plastic envelope and attached to the inner portion of each controller cabinet door.

Electrical equipment requiring modifications to conform to the contract shall have such modifications made at the factory before shipment to the project.

(6)	Valve Assembly Unit.     The valve assembly unit shall be of the same size as the pipeline that said unit serves.

(B) 	Water Service Connection.     Install the water service connection according to the requirements of the appropriate County Water Supply or governing agency.     Furnish and install the service lateral,  service connection,  meter,  meter box,  shut-off valve,  valve box and miscellaneous items necessary to complete the connection.     This includes excavation,  backfilling and tapping into the water main.

(C)		Relocation of Existing Sprinkler Lines.     Reinstall the indicated sprinkler lines at the new locations according to Subsection 616.03(A) - Installation.     If the Contractor cannot reuse the existing lines,  install new material.

The Contractor may use compression type fittings to connect new lines to existing lines.

Furnish and install a valve box at each relocated valve or multiple valve installations.

(D)		Electric Service.     The electric company will provide electric services to  the irrigation system from its facilities or existing facilities shown in the contract.     The electric services includes the equipment and features shown in the contract.     Apply to the electric company for the  required  services under the applicable rate schedule.     The Engineer will pay such charges the electric company levies.     The Contractor shall pay energy charges up to the time of final acceptance of the project.

(E)		Field Test.     Before the acceptance of the work,  conduct the following tests on the automatic sprinkler system circuits in the presence of the Engineer:

(1)	Test for continuity of each circuit.

(2)	Test for grounds in each circuit.

(3)	A megger test on each circuit between the circuit ground.   The insulation resistance shall not be less than the values specified in Section 110-20 of the Code.

(4)	A functional test to show that the system functions as specified or as intended herein.

Replace or repair faulty material or installation revealed by these tests according to the contract.     Repeat the same tests until no fault appears.

(F)		Sprinkler Heads.     Install the sprinkler heads at the locations shown in the contract or as modified and accepted by the Engineer.

The Contractor shall locate:

(1)	lawn spray heads or lawn pop-up spray heads four inches away from curbs,  sidewalks,  and pavements;

(2)	shrubbery spray heads 12 inches away from curbs,  sidewalks and pavement;  and

(3)	jet sprinkler heads or rotary  pop-up jet sprinkler heads five feet away from curbs,  sidewalks,  edge of shoulder or pavement or

(4)	as specified by the Engineer.

Install lawn pop-up spray heads and rotary pop-up jet sprinkler heads on swing joints or flexible swing joints.

(G)		Installation of Electrical Materials.

(1)	Equipment List and Drawings.     Within 30 days following the award of the contract,  submit for acceptance 6 copies of a list of materials and equipment that the Contractor will incorporate in the work.     The list shall include the name of the manufacturer,  data and catalog number of equipment,  detailed scale  drawings and wiring diagrams of the systems and proposed deviations from the contract. If required,  submit for  acceptance samples of the materials that the Contractor will use at no cost to the State.

(2)	Excavation and Backfill.     Excavation and backfill shall conform to Section 206 - Excavation and Backfill for Conduits and Structures.

(3)	Concrete for Transformer and Equipment Cabinet Pads,  Cabinet Bases,  and Conduit Encasement.     Concrete for transformer and equipment cabinet pads,  cabinet bases,  and conduit encasement shall be Class B.     They shall conform to Section 601 - Structural Concrete.     Reinforcing steel shall conform to Section 602 - Reinforcing Steel.     Welded wire fabric reinforcement shall conform to Subsection 709.01(C).

Forms shall be true to the lines and grades as accepted.  Forms shall be rigid.     Brace the forms securely in place.     Place the conduits and anchor bolts in the proper  position  and to the proper height.     Hold the conduits and anchor bolts in place with a template until the concrete sets.     Allow the concrete pads to cure for 7 days and the concrete for conduit encasement to cure for 72 hours.

Concrete pads shall be level and have a steel trowel finish.  Notify the electric company 24 hours before placement of concrete for transformer pads or conduit encasement.

*	(4)	Circuits.

(a)	Buried Conductors.     The Contractor may bury or install circuits operating at a nominal potential of 30 volts directly or in conduit.     Unreel direct burial  wires and cables alongside the trench and place carefully on the bottom of the trench.     The Engineer will not permit unreeling and pulling the cable into the trench from one end.     Before backfilling,  verify that the cable is free of kinks and sharp bends.

The Engineer will permit splices only in electrical pullboxes marked "Electric" or valve boxes housing electric control valves.     Make the splices to provide a watertight joint of dielectric value at least equal to the conductor insulation.

Leave at least two feet of slack in each conductor at each splice and at each remote control valve.     Bundle directly buried wires with nylon straps at five-foot intervals.

(b)	Conductors in Conduits.     Install circuits operating at a potential above 30 volts nominal in conduit.     Before installing the wire or cable in conduit,  pull a suitable wire brush,  swab and mandrel through the conduit to remove extraneous matter.     Verify that the conduit system is free of obstructions.     Pull the cable directly into the conduit from the shipping coil or reel before installation.     Do not uncoil and lay the cable on the ground.     Make the pulls in one direction. Use only lubricants recommended by the manufacturer of the wire or cable or accepted by the Engineer.     Do not leave the wires and cables under tension  nor tight against bushings or fittings.     When using pulling grips,  remove the damaged ends when pulling the wire or cable.     Do not pull the cable with its end open.     Maintain the seal.

Cables shall be continuous from pulling  point to pulling point.     The Engineer will not permit splices  elsewhere.  Make splices and taps with standard splicing kits of type recommended by the cable manufacturer.     Splices shall be waterproof and of dielectric value at least equal to that of the insulation of the conductors joined.

(c)	Conductors.     Conductors shall be of the size shown in the contract or larger as recommended by the manufacturer of the controllers furnished for this project.

Tag  each  conductor  in each pullbox and each conductor terminal at each controller and remote control valve with a small permanent identification tag or band.     The tags or bands shall be embossed,  non-ferrous metal,  or rigid plastic.     The embossed symbols shall contrast with the background color.     Identification on each tag or band shall include the controller station,  and number or letter designation of the controller serving the remote control valve.

(d)	Bonding and Grounding.     Ground noncurrent-carrying parts of the electrical system,  including metallic portions of conduit systems,  equipment and device enclosures,  and equipment frames.

(e)	Conduits.     Metallic conduit shall be rigid zinc-coated steel.     Non-metallic conduit shall be PVC conduit or bituminous-fiber duct (BFD).     Non-metallic conduit encased in concrete shall be PVC Schedule 40,  thin wall type for the BFD kinds.     Non-metallic conduit directly buried shall be PVC Schedule 80,  heavy wall type for the BFD kind.     Apply the conduit types shown in the contract.

Install the rigid metal conduit according to Article 346 of the Code.     Use white and tinted ready-mix paint on the threads of joints.     Repair the zinc-coated surfaces according to Subsection 501.03(G)(2) - Repairing of Damaged Zinc-Coated Surfaces.

Cut rigid PVC conduit with a hack-saw.     Square and trim the cut ends to remove rough edges.     Construction shall be of the solvent-weld type.     Make the solvent-weld joints according to the conduit manufacturer's recommendations and as accepted by the Engineer.     The  Engineer will permit preassemblying sections of conduits.

Cut the bituminous-fiber lengths with tapering tools recommended by the manufacturer.     Couplings shall be of the same material as the conduit that the couplings join.

Do not use such force as to damage the coupling.  Install the ducts to drain toward either one or both pullboxes or manhole.

Make directional changes in non-metallic conduit runs with curved equipment using accepted deflection couplings or with short lengths of straight ducts and couplings.     The deflection angle between two adjacent lengths of duct shall not exceed 6O nor shall the bends give a radius of less than 12 times the nominal size of the conduit unless using factory-made ells.

Use only hand shovels in compacting the concrete jacket unless the Engineer authorizes other methods.     Cure the concrete for at least 72 hours before permitting vehicular traffic to run over the concrete.

(5)	Pullbox.     Space the pullboxes shown in the contract or at a maximum spacing of 250 feet.     Install pullboxes with their tops one inch above the surface of the surrounding grade. In concrete walks or traffic islands,  flush the top of the pullboxes with the surrounding grade.

(I)		Water Service.     Arrange with the appropriate County Water Department for the water service.     The Contractor shall pay for the water and service charges during the period of use of the sprinkler system.     For water service from existing State water system,  the Contractor shall install a water meter to establish the Contractor's prorate usage and cost.

(J)		Acceptance.     The Engineer will not accept the sprinkler system until the end of the plant establishment period.     The sprinkler system shall be operating according to the contract for the section the Engineer is accepting.

Operate the automatic type sprinkler system in the automatic mode for at least three weeks before acceptance.     Repair the breakdowns in the system occurring during this period at no cost to the State.

(K)		Workmanship.     Install materials and equipment according to the contract.     Remove and replace material when specified in writing by the Engineer at no cost to the State.

A licensed plumbing Contractor or an experienced journeyman plumber shall do the irrigation pipe work.     A Licensed Electrical Contractor or an experienced journeyman electrician shall do the electrical work.     The contract defines plumbing and electrical work and the Contractor shall conform to "Title 16,  Chapter 80,  Rules Relating to Electricians and Plumbers,  Chapter 448E, HRS",  and "Chapter 448E,  HRS,  Electricians and Plumbers".

Iinstall sprinkler systems and automatic sprinkler control systems according to the contract.

616.04	Method of Measurement.

(A)	Irrigation system will be paid on a lump sum basis.     Measurement for payment will not apply.

(B)	The Engineer will measure components of the system per each in accordance with the contract documents.

616.05	Basis of Payment.     The Engineer will pay for the accepted pay items listed below at the contract price per pay unit as shown in the proposal schedule.          Payment will be full compensation for the work prescribed in this section and the contract documents.

The Engineer will pay for each of the following pay items when included in the proposal schedule:

Pay Item		Pay Unit

Permanent Irrigation System	Lump Sum

Temporary Irrigation System	Lump Sum

Components of the System	Linear Foot,  Each

The Engineer will pay for:

(1)	80 percent of the contract bid price upon completion of the system.

(2)	20 percent of the contract bid price upon completion of the plant establishment period.

The Engineer will pay for the copper service laterals and copper service connections under Section 624 - Water System.

The Contractor shall pay for the water used before the acceptance of the project or until the termination of the maintenance period for the plantings,  whichever is later.”

# END OF SECTION 616