Amend Section 622 - Roadway Lighting System to read as follows:

“SECTION 622 - ROADWAY LIGHTING SYSTEM

622.01	Description.     This work includes furnishing and installing a roadway lighting system and sign lighting system according to the contract.

This work includes furnishing and installing metal lamp posts with brackets, luminaires,  breakaway support couplings,  slip base inserts,  series to multiple  transformers,  lamps,  electrical conductors and conduits,  fittings,  pole line hardware insulators substation equipment,  concrete bases,  pullboxes,  and other materials  necessary for operating and controlling the roadway lighting and sign lighting  systems  and for salvaging and relocating existing roadway lights and furnishing and installing all materials necessary to connect the relocated lights to the existing light circuits according to the contract.

Furnish and install the incidental parts necessary to complete the roadway lighting and sign lighting systems as though the contract showed such parts.

Electrical equipment shall conform to the NEMA Standards.     Material and workmanship shall conform to the latest requirements of the "National Electrical Code,"  herein referred as the Code;  General Order Nos. 6 and 10,  of the Hawaii Public  Utilities Commission;  the standards of the ASTM;  the ANSI;  Local Joint Pole  Agreement;  local power company rules;  and local ordinances that may apply.

622.02	Materials.     Materials shall conform to the following:

Dark Green Enamel Paint	708.03

Welded Wire Fabric Reinforcement	709.01(C)

Pullboxes	712.06(B)

Conduits	712.27

Light Poles	712.28

Luminaires	712.29

Mast Arms	712.30

Expressway Sign Brackets	712.31

Light Sources	712.32

Isolating Transformers	712.33

Cables, Conductors and Wires	712.34

Disconnect and Protective Devices	712.35

Photo Control	712.36

Substation equipment shall be according to the contract.

Concrete shall conform to Section  601 - Structural Concrete and shall be Class B.

Anchor bolts and steel plate covers shall be structural steel conforming to ASTM A 325 and A 36 respectively.     Zinc-coat the anchor bolts if exposed.

Crossarms,  hardware,  and anchoring materials shall be of a type normally stocked and used for similar purpose by local public utility companies.

Materials will be subject to inspection.     Failure of the Engineer to note faulty material or workmanship during construction will not relieve the responsibility of the Contractor for removing or replacing such materials and redoing the work at no cost to the State.

622.03	Construction Requirements.

(A)		Equipment List and Drawings.     Within 10 days following the award of the contract,  the Contractor shall submit to the Engineer for acceptance 6 copies of a list of materials and equipment that the Contractor will incorporate in the work.     The list shall include the name of the manufacturer,  size and catalog number of the unit,  detailed scale drawings and  wiring diagrams of special equipment,  and proposed deviations from the contract.     If required,  submit for acceptance samples of the material that the Contractor will use at no cost to the State.

Upon completion of the work,  submit an ‘As Built’ plan showing in detail construction changes.

(B)		Excavation and Backfill.     Excavation and backfill shall conform to Section 206 - Excavation and Backfill for Conduits and Structures.

Excavate carefully to prevent damage to pavements,  sidewalks,  and  other improvements.

(C)		Installation.

(1)	Foundations.     Concrete for foundations of metal lamp posts shall be Class B.

Locations of metal lamp posts shown in the contract are approximate only.     The Engineer will decide the exact location in the field.

Forms shall be true to the lines and grades as accepted.  Forms shall be rigid and securely braced in place.     Place the conduit ends and anchor bolts in proper position,  placed in proper  height,  and held in place by a template until the concrete sets.    Cure the concrete for not less than 72 hours.

(2)	Metal Lamp Standards.     Install each metal lamp standard on a concrete foundation.     Set the shaft precisely vertical by adjusting the two nuts on each anchor bolt,  while the bracket shall be perpendicular to the roadway centerline.

After the lamp standard is in its proper position,  place the grout under the base plate shown in the contract.     Form the exposed portions to present a neat appearance.

Grout includes one part by volume of portland cement and three parts of beach sand.

Install metal lamp standards with breakaway design features at the locations shown in the contract.     install the standards with breakaway design features according to the manufacturer's recommendations and shown in the contract.

(3)	Mast Arms.     install each mast arm on the wood pole shown in the contract.     The mast arms shall be in a plane perpendicular to the roadway centerline.

(4)	Luminaires.     install the roadway lighting luminaires on lamp posts and mast arms with the vertical axis perpendicular to the roadway and longitudinal axis parallel to the roadway centerline.

Install the luminaires at pedestrian stairways,  underpasses and signs shown in the contract.

(5)	Circuits.     Encase the cables installed underground or in concrete rigid barrier type guard rail in conduits or other accepted encasement.

Before installing the wires and cables in conduits,  pull a wire brush,  swab and mandrel through each conduit for the removal of extraneous matter and verification of the absence of obstructions and debris from the conduit system.

Pull the cables directly from their cores or reels into the conduits.     Do not pull off and lay the cable on the ground before installation.     Make the pulls in one direction only.     Lubricants used shall be as recommended by the cable manufacturer or accepted by the Engineer.

Do not leave wires or cables under tension nor tight against bushings or fittings.     Remove damaged ends resulting from the use of pulling grips soon after pulling the cable.     Maintain the cable end seals.     Do not pull open-ended cables through the conduits.     Cables shall be continuous from pulling point to pulling point.     The Engineer will not permit splices from pulling point to pulling point.     Make splices,  taps and terminations with pressure-indented connectors or lugs as appropriate or specified in the contract.

When requiring splicing,  join the conductors by a ‘western union’ type splice or by using an accepted connector.     Use the connectors for splicing conductors,  No. 8 AWG or larger.     Solder the "western union" type splice by the pouring or dipping method. Cable splices and termination shall be according to the cable manufacturer's recommendation.     Submit the cable manufacturer's splicing instruction sheets for acceptance.

Trim the conductor insulation to a conical shape.     Roughen the conductor insulation before applying splice insulation.     Splice insulation includes layers of thermoplastic electrical insulating tape not over 0.007 inches thick conforming to Federal Specification MIL-7798.     Apply the splice insulation a thickness equal to and well lapped over the original insulation.     For high voltage and multiple lighting conductor splices,  apply two layers of synthetic oil resistant rubber tape conforming to ASTM D 119 over each conductor before placing the thermoplastic tape.     Then cover the splice well with at least two layers of asphaltic impregnated open mesh fabric tape and a coating of high grade insulating paint or similar material.     Leave at least 2 feet of slack for  each conductor at each splice.

Coil at least 5 feet of slack neatly near each lamp post foundation at both ends of each cable run.

String the overhead line wires according to Chart No. 1,  General Order 6,  Rules for Overhead Electric Line Construction as amended,  by the Hawaii Public Utilities Commission.

Wiring on the surface of wood poles shall be in rigid steel conduits from ground level to 8 feet above ground and in PVC Schedule 80 conduits from above 8 feet.

(6)	Secondary Connections.     Make the connections from the secondary power supply line to fuse boxes with aluminum or copper cable to match the existing secondary cable material.     Sizes shall be as specified in the contract.

(7)	Bonding and Grounding.     Secure the metallic cable sheaths,  conduits and lamp posts mechanically and electrically to form a continuous system.     Ground them effectively as specified in the Code and in the contract.

(8)	Pullboxes.     Install pullboxes at the locations shown in the contract.

install pullboxes so that the covers are level with the curb or sidewalk grade or 1 inch above the existing ground.

Give frames and covers two coats of asphaltic base paint after installation.

(9)	Conduits.     Lay the zinc-coated rigid steel and polyvinyl chloride (PVC) conduits carefully in trenches prepared to receive the conduits.     Conduits under roadway areas and driveways shall be PVC,  Schedule 80 or shown in the contract.

Lay the conduit that will be placed in concrete structure or encased in concrete to the required lines and grades.     Support the conduit rigidly in place by  masonry material,  manufactured conduit spacers,  or other accepted means.     Wire the conduit so that the Contractor will not dislodge the conduit during the placing and tamping of the concrete.     The thickness of the concrete around the conduits shall be shown in the contract.     Use only hand shovels in compacting the concrete.     Cure the concrete  jackets for at least  72 hours before permitting vehicular traffic.

Install the rigid steel conduit according to Article 346 of the Code.     Use white and tinted ready-mixed paint on the threads of joints.     Repair zinc-coated surfaces according to Subsection 501.03(G)(2) - Repairing of Damaged Zinc-Coated Surfaces.

Install rigid PVC conduit according to Article 347 of the Code     PVC conduit connections shall be of the solvent-weld type.     Make solvent-weld joints according to the conduit manufacturer's recommendations and as accepted by the Engineer.     The Engineer will permit pre-assemblying sections of conduit.

Make directional changes in non-metallic conduit runs such as bends and changes to clear obstructions with curved segments using accepted deflection couplings or with short lengths of straight ducts and couplings.     The deflection angle between two adjacent lengths of duct shall not exceed 6O and the bends shall not have a radius of less than 12 times the nominal size of the conduit unless using factory-made ells.

Thread the fittings for connecting non-metallic conduits to rigid metal conduits on the side that will be connected to the metal conduit.      Metal conduits entering pullboxes shall end in insulating grounding bushings.     Non-metallic conduits shall end in end bells.

Cap or plug and mark the ends of conduits shown or specified.     Provide each conduit run with a No     10 gage flexible zinc-coated pull wire or 1/8 inch polyolefin line extending uninterrupted through handholes for the entire length of run.     Double an additional 2 feet of wire or polyolefin line back into the conduit at both ends of the run

Ends of conduit runs shall extend at least 24 inches past the face of curb or edge of pavement,  unless the ends end in pullboxes.     Locate the ends accurately by special markers,  markings on curbs or as specified by the Engineer.

Keep the interior of conduits clean during the construction. Plug the ends of conduits temporarily to keep the ends clear during construction.     Install the conduits to drain toward a pullbox.     The Contractor may consider a single run to drain toward both ends.

(D)		Painting.     Furnish the metal poles and mast arms in natural finish.      The metal poles and mast arms require no painting.

Paint expressway sign brackets specified in Subsection 712.31 - Expressway Sign Brackets.

(E)		Electric Service.     Apply for electric service at each location shown in the contract and shall comply with the power company's requirements.     The Engineer will unmeter the service according to Schedule F for multiple service.

Install,  on multiple circuits,  a laminated black and  white plastic identification tag to meet the local power company's requirements at each source,  where the State takes multiple service and on each wood pole or metal lamp post supporting a luminaire.

Provide the secondary circuit extensions to the power company's service.     The Engineer will pay for permanent service connections made by the power company.

During relocation,  reconstruction or other improvements of existing roadway lighting facilities,  keep the existing roadway lighting system operational in its entirety during hours of darkness.     Schedule the work accordingly and provide a temporary lighting  system if necessary,  to keep the project area illuminated during the hours of darkness.

(F)		Field Test.     Before acceptance of the work,  make the following tests on lighting circuits,  in the presence of the Engineer.

(1)	Test for continuity of each circuit.

(2)	Test for grounds in each circuit.

(3)	A megger test on each circuit between the circuit and round. The insulation resistance shall not be less than the values specified in Table 622-I when measured with an instrument having a voltage rating of 500 volts.

| TABLE 622-I - INSULATION RESISTANCE |
| --- |
| Cable or Circuit | Minimum Resistance (ohms) |
| No.14 - No.12 wire | 1,000,000 |
| 25 to 50 amperes | 250,000 |
| 51 to 100 amperes | 100,000 |
| 101 to 200 amperes | 50,000 |
| 201 to 400 amperes | 25,000 |
| 401 to 800 amperes | 12,000 |
| over 800 amperes | 5,000 |

(4)	A functional test to show that each part of the system functions according to the contract.

Correct the faults in the material or the installation revealed by these tests at no cost to the State.     Repeat the tests until no fault appears.

(G)		Salvaging Electrical Equipment.     The contract directs the Contractor to Section 202 - Removal of Structures and Obstructions,  regarding existing highway facilities.     When shown in the contract or specified by the Engineer,  remove and salvage the existing electrical equipment including luminaires,  standards,  mast arms,  ballasts,  transformers,  service equipment,  and pullboxes,  otherwise the existing electrical equipment shall become the property of the Contractor and the Contractor shall remove and dispose of the existing electrical equipment at no cost to the State.

Underground conduits,  conductors and foundations not reused in the work shall become the property of the Contractor.     Remove them from the highway right-of-way at no cost to the State.

When abandoning a foundation in-place on outside the roadbed area,  remove the top of the foundation,  anchor bolts and conduits to a depth of 6 inches below the surface of the ground.     Backfill the resulting hole with material equivalent to the surrounding material.

When reinstalling salvaged electrical equipment,  furnish and install the materials,  equipment and incidentals necessary to complete the work.

Clean and relamp the lighting fixtures that will be reinstalled.

When the existing materials and equipment that the Contractor plans to relocate is not according to the contract,  replace them with new material and equipment.     The Engineer will pay for them as extra work according to Subsection 104.03 - Extra Work.

Salvage and stockpile the existing equipment removed and not reused in the work at the work site.

622.04	Method of Measurement.     The lighting system will be paid on a lump sum basis.     Measurement for payment will not apply.

622.05	Basis of Payment.     The Engineer will pay for the accepted lighting system on a contract lump sum basis.     Payment will be full compensation for the work prescribed in this section and the contract documents.

The Engineer will pay for the following pay item when included in the proposal schedule:

Pay Item	Pay Unit

____________________ System	Lump Sum

The Engineer will pay for hauling and stockpiling of salvaged materials and equipment off the right-of-way as specified by the Engineer in accordance with Subsection 104.02 - Changes.”

# END OF SECTION 622