Make the following section a part of the Standard Specifications:

# “SECTION 647 – FIBER OPTIC CABLE

647.01	Description.     This section applies to the installation of fiber optic cable in accordance with the contract documents.

There shall be a fiber optic cable Subcontractor, who shall have at least three years experience in installing fiber optic systems over $250,000, specifically for outdoor overhead joint-pole and underground in traffic-highway applications.     The fiber optic cable Subcontractor shall be responsible for testing all fiber optic cables to provide a documented optical budget loss analysis for each link to and from a hub station.     The fiber optic cable Subcontractor shall be responsible for all hookup,  assignments,  dedication,  testing,  matching,  and splicing of the fiber optic cables,  unless otherwise indicated.     All fiber optic splice points shall be spliced color-for-color whenever matching pairs are available.     The fiber optic cable Subcontractor shall be fully responsible for all splices,  budget loss,  attenuators,  appropriate fiber hardware,  accessories,  and pigtail connections for a fully operational system.     All other hardware, equipment, and labor necessary shall be considered incidental.

647.02	Material.     The fiber optic cables, which will be used to transmit video and data signals,  will consist of single-mode fibers.     Cables will be installed in existing conduits and overhead in the gain area reserved for the traffic signal systems under joint pole agreements.     The Contractor shall furnish and install fiber optic cable suitable, and meeting standards, for underground and aerial lashing installations.     The fiber optic cables shall meet the following specifications:

The cable shall meet the requirements of the United States Department of Agriculture (USDA) Rural Utilities Service (RUS) 7 CFR 1755.900 and shall be included in the most current ‘USDA List Of Acceptable Materials For Use On Telecommunications Systems Of RUS Borrowers’.

  - Single-mode Fiber.     The single-mode fiber utilized in the cable specified herein shall be dispersion unshifted and conform to the following specifications:

Cladding diameter: 125 μm ( 1.0 μm

Core-to-cladding offset:  < 0.6 μm

Cladding Non-circularity:  < 1.0%

Coating diameter:  245 ( 10 μm

Colored fiber diameter:  Nominal 250 μm

Attenuation uniformity:  No point discontinuity greater than 0.10 dB at either 1310 nm or 1550 nm.

Attenuation at the water peak:  The attenuation at 1383 ( 3 nm shall not exceed 2.1 dB/kM.

Cutoff wavelength: The cabled fiber cutoff wavelength shall be < 1260 nm.

Mode-field diameter:	9.30 ( 0.50 μm at 1310 nm

10.50 ( 1.00 μm at 1550 nm

Zero Dispersion wavelength:  < 1301.5 nm

Zero Dispersion Slope:  < 0.092 ps/(nm2kM)

Fiber polarization mode dispersion:  < 0.5ps/kM

The coating shall be a dual layered, UV cured acrylate applied by the fiber manufacturer.     The coating shall be mechanically strippable.

  - Fiber Specification Parameters.     Required fiber grade:  Maximum individual fiber attenuation.

Single mode – The maximum dispersion shall be ≤ 3.2 ps/nmkM from 1285 to 1330 nm and shall be < 18 ps/nm-kM at 1550 nm.

All optical fibers shall be proof tested by the fiber manufacturer to a minimum load of 0.7 GN/m2 (100 kpsi).

  - Specifications for Outdoor Cable Construction.     Optical fibers shall be inside a loose buffer tube in groups of 12.     Optical fibers shall be mechanically strippable.     Gel filled cables shall not be used.     The fiber shall be colored with ultraviolet (UV) curable links.     Each fiber shall be distinguishable by means of color coding in accordance with TIA/EIA-598-A, “Optical Fiber Cable Color Coding.”

Loose buffer tubes shall also be colored with distinct and recognizable colors in accordance with TIA/EIA-598-A, “Optical Fiber Cable Color Coding” and shall be marked Single mode.     Fillers may be included in the cable core to lend symmetry to the cable cross section where needed.     Cable construction shall utilize dielectric strength members.

Cable jacket shall be a PVC material that is fungus, water and UV resistant.     The jacket shall be marked with the manufacturer’s name, sequential meter or foot marking, month and year of manufacture,.

The maximum pulling tension shall be 2700 N (608 Ibft) during installation (short term) and 890 N (200 Ibft) long term installed.

The shipping, storage, and operating temperature range of the cable shall be -40C to +70C.

  - Quality Assurance Provision.     All cabled optical fibers > 1000 meters in length shall be 100% attenuation tested.     Attenuation of each fiber shall be provided with each cable reel.

The cable manufacturer shall be ISO 9001 registered.

  - Packaging.     Top and bottom ends of the cable shall be available for testing.

Both ends of the cable shall be sealed to prevent the ingress of moisture.     Each reel shall have a weather resistant reel tag attached identifying the reel and cable.

The reel tag shall include the following information:

Cable number		Gross Weight

Shipped length in meters 	Job order number

Product Number 		Date cable tested

A cable data sheet shall accompany each cable.     Cable data shall include manufacturer number, billable length, bandwidth specs and measured attenuation of each fiber.

672.03	Construction Requirements.

(A)	Equipment List and Drawings.     The Contractor shall submit the equipment list in accordance with Section 105 – Control of Work.

The Contractor shall submit a fiber optic cable-pulling plan for review and acceptance by the Engineer prior to beginning fiber optic cable installation.     The Contractor shall not install fiber optic cable without the Engineer's acceptance of the pulling plan.     The fiber optic cable-pulling plan shall include:

    - Location of start and end of pulls,

    - Location of cable reel trailers during installation,

    - Location of any "figure-eight" of fiber optic cable, and

    - Location of staged equipment.

Upon completion of the work, submit an ‘As Built’ or corrected plan showing in detail the following:

    - Construction changes,

    - Location and attenuation of every event along the installed fiber optic cable,

    - Index of refraction of installed fiber,

    - Fiber optic cable index of refraction, and

    - Sequential fiber optic cable markings at each pullbox, cabinet, and splice closure.

(B)	Excavation and Backfill.     Excavation and backfill shall conform to Section 206A - Excavation and Backfill for Miscellaneous Facilities.

The Contractor shall be responsible for the repair of any damage to pavements, sidewalks and other improvements.     Place the material from the excavation to prevent damage and obstruction to vehicular and pedestrian traffic and interference with surface drainage.

(C)	Fiber Optic Cable.     The fiber optic cable Subcontractor shall install the new fiber optic cable overhead on existing power poles and underground in conduits as shown in the contract documents.     The Contractor will be responsible for all work and equipment required to install the messenger cable (when there is not already existing messenger cable) on existing joint poles for the overhead portion of the fiber installation.     For the underground portion, the Contractor will be responsible for furnishing and pulling the new fiber in ductlines using a breakaway swivel to prevent exceeding the tensile load during installation.

All fiber optic splices shall be fusion splices.     Mechanical splices shall not be used.     Fiber optic splice locations are permitted only at splice points where splice cabinets are shown on the plans.     Fiber optic fibers shall be spliced in every splice cabinet location,  and it is the responsibility of the Contractor to maintain a continuous run throughout the system.     The Contractor shall leave a minimum of 20-feet of cable service loops at every cabinet or splice location, or utilize aerial cable snowshoes for overhead storage.

Provide documented historical cable pulling data indicating tensile forces exerted on the cable during the installation.     Any tension measurements,  which exceed the manufacturer's recommendation, will be considered means for the cable rejection.     The fiber optic cable Subcontractor shall be fully responsible for the quality and integrity of the installed cable and the operability of the final fiber optic cable product.     All fibers shall be spliced at camera cabinets, hubs, and splice cabinets and shall have no more than 0.07 dB loss per splice based on the appropriate system operating wavelength.

The Contractor shall complete all required fiber optic splices prior to final testing and acceptance.     As part of the final testing and acceptance, submit optical time domain reflectometer (OTDR) readings in both hardcopy and electronic formats (such that it can be examined using the manufacturer's OTDR software) to the Engineer for review.     Testing shall be conducted on all single mode fibers at 1310nm and 1550nm.     Power meter attenuation testing should be performed at dual wavelength, bi-directionally.

All necessary equipment and plug-in,  fiber optic pigtails,  fittings,  enclosures,  and work to complete an operational system shall be furnished and installed by the Contractor,  unless otherwise indicated,  at no increase in contract price or contract time.

(D)	Services Provided By The County.     The City and County of Honolulu,  Department of Transportation Services (DTS) will be responsible for all splices and connections in DTS pullboxes and DTS cabinet locations where indicated in the contract documents.

The Contractor shall be responsible for the following:

(1)	Arrange for phases of work with DTS or as specified by the Engineer.

(2)	Give at least seven calendar days of advance notice to DTS when phases of the work require its services.

(E)	Restoring Pavements and Other Improvements.     Restore the existing pavements and other improvements such as driveways,  sidewalks,  curbs and gutters disturbed by excavation to their original condition in accordance with the contract documents.     Materials used for restoration work shall be equal to or better in quality than the materials the Contractor will replace,  and matching in thickness,  texture,  and color whenever applicable.     The grades of the restored surfaces shall conform to the existing grades.

(F)	Warranty.     Materials and equipment installed for permanent construction shall be new.     The contract contemplates the use of first-class material and equipment throughout the performance of the contract.

Secure from the manufacturer(s),  a warranty or warranties guaranteeing equipment from defects in materials, design and workmanship for not less than 12 months from the date of acceptance.

When requiring adjustments or repairs during the warranty period, adjust or repair the existing unit within 24 hours from the time of notification.

When requiring repairs that need factory corrections during the warranty period, replace the existing unit with an accepted temporary operational replacement unit within 24 hours from the time of notification until the Contractor can install the new unit.     Install the new, identical non-defective unit within 30 days from the time of notification.

647.04	Method of Measurement.     Fiber optic cables will be paid on a lump sum basis.     Measurement for payment will not apply.

647.05	Basis of Payment.     The Engineer will pay for the accepted fiber optic cables on a contract lump sum basis.     Payment will be full compensation for the work prescribed in this section and the contract documents.

The Engineer will pay for the following pay item when included in the proposal schedule:

Pay Item 	Pay Unit

Fiber Optic Cable 	Lump Sum”

# SECTION 647